## energy-storage-database
technology | parameter | value | unit | source | type | note | ref_size_MW | EP_ratio_h | year | currency_year | type | carrier_store | carrier_in | carrier_out | p_store_bar | p_in_bar | p_out_bar | t_store_celsius | t_in_celsius | t_out_celsius | purity_store | purity_in | purity_out
Lithium-Ion-LFP-Energy | investment | 109.45 | $/kWh | 25 | DC storage block | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | investment | 27.57 | $/kWh | 25 | DC storage BOS | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Power | investment | 64.62 | $/kW | 25 | Power Equipment | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Power | investment | 5.78 | $/kW | 25 | Controll and Communication | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | investment | 35.19 | $/kWh | 25 | System integration | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | investment | 42.26 | $/kWh | 25 | EPC | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | investment | 50.71 | $/kWh | 25 | Project Development | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Power | investment | 21.05 | $/kW | 25 | Grid integration | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | FOM | 0.11855 | $/kWh-year |  | derived | 0.43 % of SB | 10 | 24 | 2030
Lithium-Ion-LFP-Power | FOM | 19.386 | $/kW-year |  | derived | 30% assumed of power components every 10 years | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | decommissioning | 0 | $/kWh | 25 |  | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Power | efficiency | 0.91935 |  | 25 | AC-AC efficiency at transformer level, 0.8452^0.5 | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Power | lifetime | 16 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | lifetime | 16 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-LFP-Energy | investment | 167.25 | $/kWh | 25 | DC storage block | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | investment | 36.92 | $/kWh | 25 | DC storage BOS | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Power | investment | 73.05 | $/kW | 25 | Power Equipment | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Power | investment | 7.75 | $/kW | 25 | Controll and Communication | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | investment | 41.48 | $/kWh | 25 | System integration | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | investment | 49.8 | $/kWh | 25 | EPC | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | investment | 59.76 | $/kWh | 25 | Project Development | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Power | investment | 24.81 | $/kW | 25 | Grid integration | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | FOM | 0.15876 | $/kWh-year |  | derived | 0.43 % of SB | 10 | 24 | 2021
Lithium-Ion-LFP-Power | FOM | 21.915 | $/kW-year |  | derived | 30% assumed of power components every 10 years | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | decommissioning | 2.65 | $/kWh | 25 |  | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Power | efficiency | 0.90879 |  | 25 | AC-AC efficiency at transformer level, 0.8259^0.5 | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Power | lifetime | 16 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-LFP-Energy | lifetime | 16 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | investment | 129.37 | $/kWh | 25 | DC storage block | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | investment | 26.68 | $/kWh | 25 | DC storage BOS | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Power | investment | 64.62 | $/kW | 25 | Power Equipment | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Power | investment | 5.78 | $/kW | 25 | Controll and Communication | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | investment | 40.16 | $/kWh | 25 | System integration | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | investment | 48.22 | $/kWh | 25 | EPC | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | investment | 57.86 | $/kWh | 25 | Project Development | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Power | investment | 21.05 | $/kW | 25 | Grid integration | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | FOM | 0.11472 | $/kWh-year | 25 | derived | 0.43 % of SB, =(C38+C39)*0.43/4 | 10 | 24 | 2030
Lithium-Ion-NMC-Power | FOM | 19.386 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years, =(C39)*0.3 | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | decommissioning | 0 | $/kWh | 25 |  | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Power | efficiency | 0.91935 |  | 25 | AC-AC efficiency at transformer level, 0.8452^0.5 | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Power | lifetime | 13 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | lifetime | 13 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2030
Lithium-Ion-NMC-Energy | investment | 197.7 | $/kWh | 25 | DC storage block | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | investment | 35.73 | $/kWh | 25 | DC storage BOS | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Power | investment | 73.05 | $/kW | 25 | Power Equipment | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Power | investment | 7.75 | $/kW | 25 | Controll and Communication | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | investment | 47.33 | $/kWh | 25 | System integration | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | investment | 56.82 | $/kWh | 25 | EPC | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | investment | 68.19 | $/kWh | 25 | Project Development | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Power | investment | 24.81 | $/kW | 25 | Grid integration | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | FOM | 0.15364 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Lithium-Ion-NMC-Power | FOM | 21.915 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | decommissioning | 2.65 | $/kWh | 25 |  | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Power | efficiency | 0.90879 |  | 25 | AC-AC efficiency at transformer level, 0.8259^0.5 | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Power | lifetime | 16 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2021
Lithium-Ion-NMC-Energy | lifetime | 16 | years | 25 |  | p.24 (p.46) | 10 | 24 | 2021
Lead-Acid-Energy | investment | 212.58 | $/kWh | 25 | DC storage block | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | investment | 33.75 | $/kWh | 25 | DC storage BOS | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Power | investment | 5.79 | $/kW | 25 | Controll and Communication | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | investment | 32.36 | $/kWh | 25 | System integration | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | investment | 35.42 | $/kWh | 25 | EPC | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | investment | 45.43 | $/kWh | 25 | Project Development | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Power | investment | 21.05 | $/kW | 25 | Grid integration | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | FOM | 0.91409 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Lead-Acid-Power | FOM | 35.295 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years | 10 | 24 | 2030
Lead-Acid-Energy | decommissioning | 12.04 | $/kWh | 25 |  | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Power | efficiency | 0.88882 |  | 25 | AC-AC efficiency at transformer level, 0.8452^0.5 | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Power | lifetime | 12 | years | 25 |  | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | lifetime | 12 | years | 25 |  | p.33 (p.55) | 10 | 24 | 2030
Lead-Acid-Energy | investment | 225.98 | $/kWh | 25 | DC storage block | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Energy | investment | 45.2 | $/kWh | 25 | DC storage BOS | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Power | investment | 133 | $/kW | 25 | Power Equipment | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Power | investment | 7.75 | $/kW | 25 | Controll and Communication | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Energy | investment | 38.14 | $/kWh | 25 | System integration | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Energy | investment | 41.75 | $/kWh | 25 | EPC | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Energy | investment | 53.54 | $/kWh | 25 | Project Development | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Power | investment | 24.81 | $/kW | 25 | Grid integration | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Energy | FOM | 0.97171 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Lead-Acid-Power | FOM | 39.9 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years | 10 | 24 | 2021
Lead-Acid-Energy | decommissioning | 16.89 | $/kWh | 25 |  | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Power | efficiency | 0.88882 |  | 25 | AC-AC efficiency at transformer level, 0.8259^0.5 | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Power | lifetime | 12 | years | 25 |  | p.33 (p.55) | 10 | 24 | 2021
Lead-Acid-Energy | lifetime | 12 | years | 25 |  | p.33 (p.55) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | investment | 157.79 | $/kWh | 25 | DC storage block | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | investment | 28.35 | $/kWh | 25 | DC storage BOS | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Power | investment | 5.82 | $/kW | 25 | Controll and Communication | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | investment | 29.72 | $/kWh | 25 | System integration | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | investment | 34.2 | $/kWh | 25 | EPC | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | investment | 39.33 | $/kWh | 25 | Project Development | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Power | investment | 21.21 | $/kW | 25 | Grid integration | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | FOM | 0.6785 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Vanadium-Redox-Flow-Power | FOM | 35.295 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | decommissioning | 19.77 | $/kWh | 25 |  | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Power | efficiency | 0.80623 |  | 25 | AC-AC efficiency at transformer level, 0.8452^0.5 | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Power | lifetime | 12 | years | 25 |  | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | lifetime | 12 | years | 25 |  | p.42 (p.64) | 10 | 24 | 2030
Vanadium-Redox-Flow-Energy | investment | 189.83 | $/kWh | 25 | DC storage block | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | investment | 37.97 | $/kWh | 25 | DC storage BOS | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Power | investment | 133 | $/kW | 25 | Power Equipment | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Power | investment | 7.8 | $/kW | 25 | Controll and Communication | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | investment | 35.03 | $/kWh | 25 | System integration | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | investment | 40.3 | $/kWh | 25 | EPC | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | investment | 46.35 | $/kWh | 25 | Project Development | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Power | investment | 25 | $/kW | 25 | Grid integration | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | FOM | 0.81627 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Vanadium-Redox-Flow-Power | FOM | 39.9 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | decommissioning | 22.95 | $/kWh | 25 |  | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Power | efficiency | 0.80623 |  | 25 | AC-AC efficiency at transformer level, 0.8259^0.5 | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Power | lifetime | 12 | years | 25 |  | p.42 (p.64) | 10 | 24 | 2021
Vanadium-Redox-Flow-Energy | lifetime | 12 | years | 25 |  | p.42 (p.64) | 10 | 24 | 2021
Ni-Zn-Energy | investment | 158 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.14 | 10 | 24 | 2030
Ni-Zn-Energy | investment | 27 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.16 | 10 | 24 | 2030
Ni-Zn-Power | investment | 64.62 | $/kW | 25 | Power Equipment | p.59 (p.81), same as Li-LFP | 10 | 24 | 2030
Ni-Zn-Power | investment | 5.78 | $/kW | 25 | Controll and Communication | p.59 (p.81), same as Li-LFP | 10 | 24 | 2030
Ni-Zn-Energy | investment | 31.67 | $/kWh | 25 | System integration | p.59 (p.81), same as Li-LFP | 10 | 24 | 2030
Ni-Zn-Energy | investment | 38.03 | $/kWh | 25 | EPC | p.59 (p.81), same as Li-LFP | 10 | 24 | 2030
Ni-Zn-Energy | investment | 45.64 | $/kWh | 25 | Project Development | p.59 (p.81), same as Li-LFP | 10 | 24 | 2030
Ni-Zn-Power | investment | 21.05 | $/kW | 25 | Grid integration | p.59 (p.81), same as Li-LFP | 10 | 24 | 2030
Ni-Zn-Energy | FOM | 0.6794 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Ni-Zn-Power | FOM | 8.5 | $/kW-year | 25 | Table 4.22 | 30% assumed of power components every 10 years | 10 | 24 | 2030
Ni-Zn-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Ni-Zn-Power | efficiency | 0.9 |  | 25 | ((0.71+0.88)/2)^0.5, mean value of range, efficiency is not RTE but single way AC-store conversion | p.59 (p.81) | 10 | 24 | 2030
Ni-Zn-Power | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Ni-Zn-Energy | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Ni-Zn-Energy | investment | 197 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.13 | 10 | 24 | 2021
Ni-Zn-Energy | investment | 30 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.15 | 10 | 24 | 2021
Ni-Zn-Power | investment | 73.05 | $/kW | 25 | Power Equipment | p.59 (p.81), same as Li-LFP | 10 | 24 | 2021
Ni-Zn-Power | investment | 7.75 | $/kW | 25 | Controll and Communication | p.59 (p.81), same as Li-LFP | 10 | 24 | 2021
Ni-Zn-Energy | investment | 41.48 | $/kWh | 25 | System integration | p.59 (p.81), same as Li-LFP | 10 | 24 | 2021
Ni-Zn-Energy | investment | 49.8 | $/kWh | 25 | EPC | p.59 (p.81), same as Li-LFP | 10 | 24 | 2021
Ni-Zn-Energy | investment | 59.76 | $/kWh | 25 | Project Development | p.59 (p.81), same as Li-LFP | 10 | 24 | 2021
Ni-Zn-Power | investment | 24.81 | $/kW | 25 | Grid integration | p.59 (p.81), same as Li-LFP | 10 | 24 | 2021
Ni-Zn-Energy | FOM | 0.8471 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Ni-Zn-Power | FOM | 10 | $/kW-year | 25 | Table 4.22 | 30% assumed of power components every 10 years | 10 | 24 | 2021
Ni-Zn-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Ni-Zn-Power | efficiency | 0.89163 |  | 25 | AC-AC efficiency at transformer level, 0.8452^0.5 | p.59 (p.81) | 10 | 24 | 2021
Ni-Zn-Power | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Ni-Zn-Energy | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Energy | investment | 277 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.14 | 10 | 24 | 2030
Zn-Br-Flow-Energy | investment | 70 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.16 | 10 | 24 | 2030
Zn-Br-Flow-Power | investment | 64.62 | $/kW | 25 | Power Equipment | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Power | investment | 5.78 | $/kW | 25 | Controll and Communication | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Energy | investment | 31.67 | $/kWh | 25 | System integration | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Energy | investment | 38.03 | $/kWh | 25 | EPC | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Energy | investment | 45.64 | $/kWh | 25 | Project Development | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Power | investment | 21.05 | $/kW | 25 | Grid integration | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Energy | FOM | 1.1911 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Zn-Br-Flow-Power | FOM | 36 | $/kW-year | 25 |  | 30% assumed of power components every 10 years, Table 4.22 | 10 | 24 | 2030
Zn-Br-Flow-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Flow-Power | efficiency | 0.83066 |  | 25 | (0.69)^0.5, efficiency is not RTE but single way AC-store conversion | p.59 (p.81), Table 4.25, | 10 | 24 | 2030
Zn-Br-Flow-Power | lifetime | 10 | years | 25 |  | p.59 (p.81), Table 4.27 | 10 | 24 | 2030
Zn-Br-Flow-Energy | lifetime | 10 | years | 25 |  | p.59 (p.81), Table 4.27 | 10 | 24 | 2030
Zn-Br-Flow-Energy | investment | 346 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.13 | 10 | 24 | 2021
Zn-Br-Flow-Energy | investment | 78 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.15 | 10 | 24 | 2021
Zn-Br-Flow-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Power | investment | 5.82 | $/kW | 25 | Controll and Communication | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Energy | investment | 29.72 | $/kWh | 25 | System integration | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Energy | investment | 34.2 | $/kWh | 25 | EPC | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Energy | investment | 39.33 | $/kWh | 25 | Project Development | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Power | investment | 21.21 | $/kW | 25 | Grid integration | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Energy | FOM | 1.4878 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Zn-Br-Flow-Power | FOM | 42 | $/kW-year | 25 |  | 30% assumed of power components every 10 years, Table 4.22 | 10 | 24 | 2021
Zn-Br-Flow-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Power | efficiency | 0.80623 |  | 25 | (0.65)^0.5, efficiency is not RTE but single way AC-store conversion | p.59 (p.81), Table 4.25, | 10 | 24 | 2021
Zn-Br-Flow-Power | lifetime | 10 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Flow-Energy | lifetime | 10 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | investment | 140 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.14 | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | investment | 25 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.16 | 10 | 24 | 2030
Zn-Br-Nonflow-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Power | investment | 5.82 | $/kW | 25 | Controll and Communication | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | investment | 29.72 | $/kWh | 25 | System integration | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | investment | 34.2 | $/kWh | 25 | EPC | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | investment | 39.33 | $/kWh | 25 | Project Development | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Power | investment | 21.21 | $/kW | 25 | Grid integration | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | FOM | 0.602 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Zn-Br-Nonflow-Power | FOM | 0.43 | $/kW-year | 25 | Table 4.22 | 30% assumed of power components every 10 years | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Power | efficiency | 0.88882 |  | 25 | (0.79)^0.5, efficiency is not RTE but single way AC-store conversion | p.59 (p.81), Table 4.25, | 10 | 24 | 2030
Zn-Br-Nonflow-Power | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Br-Nonflow-Energy | investment | 175 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.13 | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | investment | 28 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.15 | 10 | 24 | 2021
Zn-Br-Nonflow-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Power | investment | 5.82 | $/kW | 25 | Controll and Communication | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | investment | 29.72 | $/kWh | 25 | System integration | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | investment | 34.2 | $/kWh | 25 | EPC | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | investment | 39.33 | $/kWh | 25 | Project Development | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Power | investment | 21.21 | $/kW | 25 | Grid integration | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | FOM | 0.7525 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Zn-Br-Nonflow-Power | FOM | 0.5 | $/kW-year | 25 |  | 30% assumed of power components every 10 years, Table 4.22 | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Power | efficiency | 0.86603 |  | 25 | (0.75)^0.5, efficiency is not RTE but single way AC-store conversion | p.59 (p.81), Table 4.25 | 10 | 24 | 2021
Zn-Br-Nonflow-Power | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Br-Nonflow-Energy | lifetime | 15 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Energy | investment | 75.2 | $/kWh | 25 | DC storage block | p.48 (p.70), text below Table 4.12 | 10 | 24 | 2030
Zn-Air-Energy | investment | 17.1 | $/kWh | 25 | DC storage BOS | p.48 (p.70), text below Table 4.12 | 10 | 24 | 2030
Zn-Air-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Power | investment | 5.82 | $/kW | 25 | Controll and Communication | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Energy | investment | 29.72 | $/kWh | 25 | System integration | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Energy | investment | 34.2 | $/kWh | 25 | EPC | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Energy | investment | 39.33 | $/kWh | 25 | Project Development | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Power | investment | 21.21 | $/kW | 25 | Grid integration | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Energy | FOM | 0.32336 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Zn-Air-Power | FOM | 23 | $/kW-year | 25 |  | 30% assumed of power components every 10 years, Table 4.22 | 10 | 24 | 2030
Zn-Air-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Power | efficiency | 0.79373 |  | 25 | (0.63)^0.5, efficiency is not RTE but single way AC-store conversion | p.59 (p.81), Table 4.25, | 10 | 24 | 2030
Zn-Air-Power | lifetime | 25 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Energy | lifetime | 25 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2030
Zn-Air-Energy | investment | 94 | $/kWh | 25 | DC storage block | p.59 (p.81), Table 4.12 | 10 | 24 | 2021
Zn-Air-Energy | investment | 19 | $/kWh | 25 | DC storage BOS | p.59 (p.81), Table 4.12 | 10 | 24 | 2021
Zn-Air-Power | investment | 117.65 | $/kW | 25 | Power Equipment | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Power | investment | 5.82 | $/kW | 25 | Controll and Communication | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Energy | investment | 29.72 | $/kWh | 25 | System integration | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Energy | investment | 34.2 | $/kWh | 25 | EPC | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Energy | investment | 39.33 | $/kWh | 25 | Project Development | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Power | investment | 21.21 | $/kW | 25 | Grid integration | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Energy | FOM | 0.4042 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Zn-Air-Power | FOM | 27 | $/kW-year | 25 |  | 30% assumed of power components every 10 years, Table 4.22 | 10 | 24 | 2021
Zn-Air-Energy | decommissioning | 0 | $/kWh | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Power | efficiency | 0.76811 |  | 25 | (0.59)^0.5, efficiency is not RTE but single way AC-store conversion | p.59 (p.81), Table 4.25, | 10 | 24 | 2021
Zn-Air-Power | lifetime | 25 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Zn-Air-Energy | lifetime | 25 | years | 25 |  | p.59 (p.81) | 10 | 24 | 2021
Compressed-Air-Adiabatic-Energy | investment | 6.11 | $/kWh | 25 | Cavern Storage | p.64 (p.86) | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Power | investment | 1061 | $/kW | 25 | Turbine, Compressor, BOP, EPC Management | p.59 (p.81) | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Energy | FOM | 0.026273 | $/kWh-year | 25 | derived | 0.43 % of SB, 4.5.2.1 Fixed O&M, p.62 (p.84) | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Power | FOM | 9.83 | $/kW-year | 25 |  | p.64 (p.86) Figure 4.14 | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Power | efficiency | 0.72111 |  | 25 | AC-AC efficiency at transformer level, 0.52^0.5 | p.59 (p.81) | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Power | lifetime | 60 | years | 25 |  | p.59 (p.81) | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Energy | lifetime | 60 | years | 25 |  | p.59 (p.81) | 1000 | 24 | 2030
Compressed-Air-Adiabatic-Energy | investment | 6.11 | $/kWh | 25 | Cavern Storage | p.64 (p.86) | 1000 | 24 | 2021
Compressed-Air-Adiabatic-Power | investment | 1061 | $/kW | 25 | Turbine, Compressor, BOP, EPC Management | p.59 (p.81) | 1000 | 24 | 2021
Compressed-Air-Adiabatic-Energy | FOM | 0.026273 | $/kWh-year | 25 | derived | 0.43 % of SB, 4.5.2.1 Fixed O&M, p.62 (p.84) | 1000 | 24 | 2021
Compressed-Air-Adiabatic-Power | FOM | 9.83 | $/kW-year | 25 |  | p.64 (p.86) Figure 4.14 | 1000 | 24 | 2021
Compressed-Air-Adiabatic-Power | efficiency | 0.72111 |  | 25 | AC-AC efficiency at transformer level, 0.52^0.5 | p.59 (p.81) | 1000 | 24 | 2021
Compressed-Air-Adiabatic-Power | lifetime | 60 | years | 25 |  | p.59 (p.81) | 1000 | 24 | 2021
Compressed-Air-Adiabatic-Energy | lifetime | 60 | years | 25 |  | p.59 (p.81) | 1000 | 24 | 2021
Pumped-Storage-Hydro-Energy | investment | 64 | $/kWh | 25 | Reservoir Construction & Infrastructure | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Power | investment | 623 | $/kW | 25 | Powerhouse Construction & Infrastructure | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Power | investment | 392 | $/kW | 25 | Electromechanical | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Power | investment | 551.67 | $/kW | 25 | Contigency Fee | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Energy | FOM | 0.2752 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2030
Pumped-Storage-Hydro-Power | FOM | 15.59 | $/kW-year | 25 |  | Figure 4.16 | 10 | 24 | 2030
Pumped-Storage-Hydro-Power | efficiency | 0.89443 |  | 25 | AC-AC efficiency at transformer level, 0.8^0.5 | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Power | lifetime | 60 | years | 25 |  | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Energy | lifetime | 60 | years | 25 |  | p.68 (p.90) | 10 | 24 | 2030
Pumped-Storage-Hydro-Energy | investment | 64 | $/kWh | 25 | Reservoir Construction & Infrastructure | p.68 (p.90) | 10 | 24 | 2021
Pumped-Storage-Hydro-Power | investment | 623 | $/kW | 25 | Powerhouse Construction & Infrastructure | p.68 (p.90) | 10 | 24 | 2021
Pumped-Storage-Hydro-Power | investment | 392 | $/kW | 25 | Electromechanical | p.68 (p.90) | 10 | 24 | 2021
Pumped-Storage-Hydro-Power | investment | 551.67 | $/kW | 25 | Contigency Fee | p.68 (p.90) | 10 | 24 | 2021
Pumped-Storage-Hydro-Energy | FOM | 0.2752 | $/kWh-year | 25 | derived | 0.43 % of SB | 10 | 24 | 2021
Pumped-Storage-Hydro-Power | FOM | 15.59 | $/kW-year | 25 |  | Figure 4.16 | 10 | 24 | 2021
Pumped-Storage-Hydro-Power | efficiency | 0.89443 |  | 25 | AC-AC efficiency at transformer level, 0.8^0.5 | p.68 (p.90) | 10 | 24 | 2021
Pumped-Storage-Hydro-Power | lifetime | 60 | years | 25 |  | p.68 (p.90) | 10 | 24 | 2021
Pumped-Storage-Hydro-Energy | lifetime | 60 | years | 25 |  | p.68 (p.90) | 10 | 24 | 2030
Gravity-Brick-Energy | investment | 148.75 | $/kWh | 25 | Gravitational Capital (SB+BOS) | p.71 (p.94), text at the bottom speaks about 15% cost reduction for 2030 compared to 2021 | 1000 | 24 | 2030
Gravity-Brick-Power | investment | 466 | $/kW | 25 | Power Equipment | p.71 (p.94), text at the bottom speaks about 0% cost reduction for 2030 compared to 2021 | 1000 | 24 | 2030
Gravity-Brick-Energy | investment | 27.73 | $/kWh | 25 | EPC Fee, Project Development, Grid integration | p.80 (p.102), Figure 4.18 | 1000 | 24 | 2030
Gravity-Brick-Power | FOM | 47 | $/kW-year | 25 |  | p.77 (p.99), Table 4.35 | 1000 | 24 | 2030
Gravity-Brick-Power | efficiency | 0.92736 |  | 25 | AC-AC efficiency at transformer level, 0.86^0.5 | p.77 (p.99), Table 4.36 | 1000 | 24 | 2030
Gravity-Brick-Power | lifetime | 41.7 | years | 25 |  | p.77 (p.99), Table 4.36 | 1000 | 24 | 2030
Gravity-Brick-Energy | lifetime | 41.7 | years | 25 |  | p.77 (p.99), Table 4.36 | 1000 | 24 | 2030
Gravity-Brick-Energy | investment | 175 | $/kWh | 25 | Gravitational Capital (SB+BOS) | p.75 (p.97), Table 4.32 | 1000 | 24 | 2021
Gravity-Brick-Power | investment | 466 | $/kW | 25 | Power Equipment | p.74 (p.96), Table 4.31 | 1000 | 24 | 2021
Gravity-Brick-Energy | investment | 31.7 | $/kWh | 25 | EPC Fee, Project Development, Grid integration | p.80 (p.102), Figure 4.18 | 1000 | 24 | 2021
Gravity-Brick-Power | FOM | 47 | $/kW-year | 25 |  | p.77 (p.99), Table 4.35 | 1000 | 24 | 2021
Gravity-Brick-Power | efficiency | 0.92736 |  | 25 | AC-AC efficiency at transformer level, 0.86^0.5 | p.77 (p.99), Table 4.36 | 1000 | 24 | 2021
Gravity-Brick-Power | lifetime | 41.7 | years | 25 |  | p.77 (p.99), Table 4.36 | 1000 | 24 | 2021
Gravity-Brick-Energy | lifetime | 41.7 | years | 25 |  | p.77 (p.99), Table 4.36 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Energy | investment | 108.8 | $/kWh | 25 | Gravitational Capital (SB+BOS) | p.71 (p.94), text at the bottom speaks about 15% cost reduction for 2030 compared to 2021 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Energy | investment | 410 | $/kW | 25 | Power Equipment | p.71 (p.94), text at the bottom speaks about 0% cost reduction for 2030 compared to 2021 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Power | investment | 27.73 | $/kWh | 25 | EPC Fee, Project Development, Grid integration | p.80 (p.102), Figure 4.18 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Power | FOM | 16 | $/kW-year | 25 |  | p.77 (p.99), Table 4.35 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Energy | efficiency | 0.90139 |  | 25 | AC-AC efficiency at transformer level, ((0.785+0.84)/2)^0.5 | p.77 (p.99), Table 4.37 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Energy | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Energy | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2030
Gravity-Water-Aboveground-Power | investment | 128 | $/kWh | 25 | Gravitational Capital (SB+BOS) | p.75 (p.97), Table 4.32 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Energy | investment | 410 | $/kW | 25 | Power Equipment | p.74 (p.96), Table 4.31 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Power | investment | 31.7 | $/kWh | 25 | EPC Fee, Project Development, Grid integration | p.80 (p.102), Figure 4.18 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Energy | FOM | 16 | $/kW-year | 25 |  | p.77 (p.99), Table 4.35 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Power | efficiency | 0.90139 |  | 25 | AC-AC efficiency at transformer level, ((0.785+0.84)/2)^0.5 | p.77 (p.99), Table 4.37 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Power | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2021
Gravity-Water-Aboveground-Energy | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2021
Gravity-Water-Underground-Energy | investment | 79.9 | $/kWh | 25 | Gravitational Capital (SB+BOS) | p.71 (p.94), text at the bottom speaks about 15% cost reduction for 2030 compared to 2021 | 1000 | 24 | 2030
Gravity-Water-Underground-Energy | investment | 1015 | $/kW | 25 | Power Equipment | p.71 (p.94), text at the bottom speaks about 0% cost reduction for 2030 compared to 2021 | 1000 | 24 | 2030
Gravity-Water-Underground-Power | investment | 27.73 | $/kWh | 25 | EPC Fee, Project Development, Grid integration | p.80 (p.102), Figure 4.18 | 1000 | 24 | 2030
Gravity-Water-Underground-Power | FOM | 16 | $/kW-year | 25 |  | p.77 (p.99), Table 4.35 | 1000 | 24 | 2030
Gravity-Water-Underground-Energy | efficiency | 0.90139 |  | 25 | AC-AC efficiency at transformer level, ((0.785+0.84)/2)^0.5 | p.77 (p.99), Table 4.37 | 1000 | 24 | 2030
Gravity-Water-Underground-Energy | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2030
Gravity-Water-Underground-Energy | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2030
Gravity-Water-Underground-Power | investment | 94 | $/kWh | 25 | Gravitational Capital (SB+BOS) | p.75 (p.97), Table 4.32 | 1000 | 24 | 2021
Gravity-Water-Underground-Energy | investment | 1015 | $/kW | 25 | Power Equipment | p.74 (p.96), Table 4.31 | 1000 | 24 | 2021
Gravity-Water-Underground-Power | investment | 31.7 | $/kWh | 25 | EPC Fee, Project Development, Grid integration | p.80 (p.102), Figure 4.18 | 1000 | 24 | 2021
Gravity-Water-Underground-Energy | FOM | 16 | $/kW-year | 25 |  | p.77 (p.99), Table 4.35 | 1000 | 24 | 2021
Gravity-Water-Underground-Power | efficiency | 0.90139 |  | 25 | AC-AC efficiency at transformer level, ((0.785+0.84)/2)^0.5 | p.77 (p.99), Table 4.37 | 1000 | 24 | 2021
Gravity-Water-Underground-Power | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2021
Gravity-Water-Underground-Energy | lifetime | 60 | years | 25 |  | p.77 (p.99), Table 4.37 | 1000 | 24 | 2021
Hydrogen-Power | investment | 425 | $/kW | 25 | Fuel Cell | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Power | investment | 350 | $/kW | 25 | Electrolyzer | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Energy | investment | 5.36 | $/kWh | 25 | Cavern Storage | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Power | investment | 39.3 | $/kW | 25 | Compressor | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Energy | investment | 39 | $/kW | 25 | Inverter | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Power | investment | 84 | $/kW | 25 | Rectifier | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Power | investment | 1.06 | $/kW | 25 | Controll and Communication | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Power | investment | 16.3 | $/kW | 25 | Grid integration | p.113 (p.135) | 10 | 24 | 2030
Hydrogen-Energy | FOM | 0.023048 | $/kWh-year | 25 | derived | 0.43 % of SB, =(C38+C39)*0.43/4 | 10 | 24 | 2030
Hydrogen-Power | FOM | 4.9405 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years, =(C45+C41+C40)*0.3+1.94 | 10 | 24 | 2030
Hydrogen-Power | efficiency | 0.69629 |  | 25 | Electrolyzer | p.111 (p.133), include inverter 0.98 & transformer efficiency 0.98 | 10 | 24 | 2030
Hydrogen-Power | efficiency | 0.48692 |  | 25 | Fuel Cell | p.111 (p.133), include inverter 0.98 & transformer efficiency 0.98 | 10 | 24 | 2030
Hydrogen-Power | lifetime | 30 | years | 25 |  | p.111 (p.133) | 10 | 24 | 2030
Hydrogen-Energy | lifetime | 30 | years | 25 |  | p.111 (p.133) | 10 | 24 | 2030
Hydrogen-Power | investment | 1320 | $/kW | 25 | Fuel Cell | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Power | investment | 1316 | $/kW | 25 | Electrolyzer | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Energy | investment | 5.36 | $/kWh | 25 | Cavern Storage | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Power | investment | 39.3 | $/kW | 25 | Compressor | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Energy | investment | 67 | $/kW | 25 | Inverter | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Power | investment | 130 | $/kW | 25 | Rectifier | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Power | investment | 1.5 | $/kW | 25 | Controll and Communication | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Power | investment | 19.89 | $/kW | 25 | Grid integration | p.113 (p.135) | 10 | 24 | 2021
Hydrogen-Energy | FOM | 0.023048 | $/kWh-year | 25 | derived | 0.43 % of SB, =(C38+C39)*0.43/4 | 10 | 24 | 2021
Hydrogen-Power | FOM | 12.9428 | $/kW-year | 25 | derived | 30% assumed of power components every 10 years, =(C45+C41+C40)*0.3+1.94 | 10 | 24 | 2021
Hydrogen-Power | efficiency | 0.69629 |  | 25 | Electrolyzer | p.111 (p.133), include inverter 0.98 & transformer efficiency 0.98 | 10 | 24 | 2021
Hydrogen-Power | efficiency | 0.48692 |  | 25 | Fuel Cell | p.111 (p.133), include inverter 0.98 & transformer efficiency 0.98 | 10 | 24 | 2021
Hydrogen-Power | lifetime | 30 | years | 25 |  | p.111 (p.133) | 10 | 24 | 2021
Hydrogen-Energy | lifetime | 30 | years | 25 |  | p.111 (p.133) | 10 | 24 | 2021
Pumped-Heat-Energy | investment | 4.6 | $/kWh | 25 | Molten Salt based SB and BOS | p.92 (p.114) |  |  | 2030
Pumped-Heat-Power | investment | 1454 | $/kW | 25 | Power Equipment | p.92 (p.114) |  |  | 2030
Pumped-Heat-Energy | investment | 5.36 | $/kWh | 25 | EPC fee | p.92 (p.114) |  |  | 2030
Pumped-Heat-Energy | investment | 0.996 | $/kWh | 25 | Project Development | p.92 (p.114) |  |  | 2030
Pumped-Heat-Energy | investment | 1.992 | $/kWh | 25 | Grid integration | p.92 (p.114) |  |  | 2030
Pumped-Heat-Energy | FOM | 0.01978 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p.103 (p.125) |  |  | 2030
Pumped-Heat-Power | FOM | 6.2522 | $/kW-year | 25 | not provided, calculated as for hydrogen | p.103 (p.125) |  |  | 2030
Pumped-Heat-Power | efficiency | 0.62 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) |  |  | 2030
Pumped-Heat-Power | lifetime | 33 | years | 25 |  | p.107 (p.129) |  |  | 2030
Pumped-Heat-Energy | lifetime | 33 | years | 25 |  | p.107 (p.129) |  |  | 2030
Pumped-Heat-Energy | investment | 5.4 | $/kWh | 25 | Molten Salt based SB and BOS | p.92 (p.114) |  |  | 2021
Pumped-Heat-Power | investment | 1532 | $/kW | 25 | Power Equipment | p.92 (p.114) |  |  | 2021
Pumped-Heat-Energy | investment | 19.89 | $/kWh | 25 | EPC fee | p.92 (p.114) |  |  | 2021
Pumped-Heat-Energy | investment | 2.529 | $/kWh | 25 | Project Development | p.92 (p.114) |  |  | 2021
Pumped-Heat-Energy | investment | 5.058 | $/kWh | 25 | Grid integration | p.92 (p.114) |  |  | 2021
Pumped-Heat-Energy | FOM | 0.02322 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p.103 (p.125) |  |  | 2021
Pumped-Heat-Power | FOM | 6.5876 | $/kW-year | 25 | not provided, calculated as for hydrogen | p.103 (p.125) |  |  | 2021
Pumped-Heat-Power | efficiency | 0.6 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) |  |  | 2021
Pumped-Heat-Power | lifetime | 30 | years | 25 |  | p.107 (p.129) |  |  | 2021
Pumped-Heat-Energy | lifetime | 30 | years | 25 |  | p.107 (p.129) |  |  | 2021
Liquid-Air-Energy | investment | 133 | $/kWh | 25 | Liquid Air SB and BOS | p.98 (p.120) |  |  | 2030
Liquid-Air-Power | investment | 908 | $/kW | 25 | Power Equipment | p.98 (p.120) |  |  | 2030
Liquid-Air-Energy | investment | 7 | $/kWh | 25 | EPC fee | p.98 (p.120) |  |  | 2030
Liquid-Air-Energy | investment | 27 | $/kWh | 25 | Project Development | p.98 (p.120) |  |  | 2030
Liquid-Air-Energy | investment | 11.3 | $/kWh | 25 | Grid integration | p.98 (p.120) |  |  | 2030
Liquid-Air-Energy | FOM | 0.5719 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) |  |  | 2030
Liquid-Air-Power | FOM | 3.9044 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) |  |  | 2030
Liquid-Air-Power | efficiency | 0.545 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) |  |  | 2030
Liquid-Air-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) |  |  | 2030
Liquid-Air-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) |  |  | 2030
Liquid-Air-Energy | investment | 157 | $/kWh | 25 | Liquid Air SB and BOS | p.98 (p.120) |  |  | 2021
Liquid-Air-Power | investment | 956 | $/kW | 25 | Power Equipment | p.98 (p.120) |  |  | 2021
Liquid-Air-Energy | investment | 8 | $/kWh | 25 | EPC fee | p.98 (p.120) |  |  | 2021
Liquid-Air-Energy | investment | 30 | $/kWh | 25 | Project Development | p.98 (p.120) |  |  | 2021
Liquid-Air-Energy | investment | 11.3 | $/kWh | 25 | Grid integration | p.98 (p.120) |  |  | 2021
Liquid-Air-Energy | FOM | 0.6751 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) |  |  | 2021
Liquid-Air-Power | FOM | 4.1108 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) |  |  | 2021
Liquid-Air-Power | efficiency | 0.525 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) |  |  | 2021
Liquid-Air-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) |  |  | 2021
Liquid-Air-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) |  |  | 2021
Sand-Energy | investment | 5.78 | $/kWh | 25 | SB and BOS, 0.85 of 2021 value | p.100 (p.122) | 1000 | 24 | 2030
Sand-Power | investment | 808.45 | $/kW | 25 | Power Equipment, 0.95 of 2021 value | p.100 (p.122) | 1000 | 24 | 2030
Sand-Energy | investment | 1.734 | $/kWh | 25 | EPC fee, Project Development, Grid integration | p.98 (p.120) | 1000 | 24 | 2030
Sand-Energy | FOM | 0.024854 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
Sand-Power | FOM | 3.4763 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
Sand-Power | efficiency | 0.52 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2030
Sand-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
Sand-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
Sand-Energy | investment | 6.8 | $/kWh | 25 | SB and BOS | p.101 (p.123) | 1000 | 24 | 2021
Sand-Power | investment | 851 | $/kW | 25 | Power Equipment | p.101 (p.123) | 1000 | 24 | 2021
Sand-Energy | investment | 2.04 | $/kWh | 25 | EPC fee, Project Development, Grid integration | p.101 (p.123) | 1000 | 24 | 2021
Sand-Energy | FOM | 0.02924 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p.100 (p.122) | 1000 | 24 | 2021
Sand-Power | FOM | 3.6593 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
Sand-Power | efficiency | 0.5 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2021
Sand-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
Sand-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
HighT-Molten-Salt-Energy | investment | 81.175 | $/kWh | 25 | SB and BOS, 0.85 of 2021 value | p.98 (p.120) | 1000 | 24 | 2030
HighT-Molten-Salt-Power | investment | 808.45 | $/kW | 25 | Power Equipment, 0.95 of 2021 value | p.98 (p.120) | 1000 | 24 | 2030
HighT-Molten-Salt-Energy | investment | 24.3525 | $/kWh | 25 | EPC fee, Project Development, Grid integration | p.98 (p.120) | 1000 | 24 | 2030
HighT-Molten-Salt-Energy | FOM | 0.34905 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
HighT-Molten-Salt-Power | FOM | 3.4763 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
HighT-Molten-Salt-Power | efficiency | 0.44 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2030
HighT-Molten-Salt-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
HighT-Molten-Salt-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
HighT-Molten-Salt-Energy | investment | 95.5 | $/kWh | 25 | SB and BOS | p.101 (p.123) | 1000 | 24 | 2021
HighT-Molten-Salt-Power | investment | 1029 | $/kW | 25 | Power Equipment | p.101 (p.123) | 1000 | 24 | 2021
HighT-Molten-Salt-Energy | investment | 28.65 | $/kWh | 25 | EPC fee, Project Development, Grid integration | p.101 (p.123) | 1000 | 24 | 2021
HighT-Molten-Salt-Energy | FOM | 0.41065 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
HighT-Molten-Salt-Power | FOM | 4.4247 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
HighT-Molten-Salt-Power | efficiency | 0.42 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2021
HighT-Molten-Salt-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
HighT-Molten-Salt-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
LowT-Molten-Salt-Energy | investment | 50.065 | $/kWh | 25 | SB and BOS, 0.85 of 2021 value | p.98 (p.120) | 1000 | 24 | 2030
LowT-Molten-Salt-Power | investment | 808.45 | $/kW | 25 | Power Equipment, 0.95 of 2021 value | p.98 (p.120) | 1000 | 24 | 2030
LowT-Molten-Salt-Energy | investment | 15.0195 | $/kWh | 25 | EPC fee, Project Development, Grid integration | p.98 (p.120) | 1000 | 24 | 2030
LowT-Molten-Salt-Energy | FOM | 0.21528 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
LowT-Molten-Salt-Power | FOM | 3.4763 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
LowT-Molten-Salt-Power | efficiency | 0.534 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2030
LowT-Molten-Salt-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
LowT-Molten-Salt-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
LowT-Molten-Salt-Energy | investment | 58.9 | $/kWh | 25 | Molten Salt SB and BOS | p.101 (p.123) | 1000 | 24 | 2021
LowT-Molten-Salt-Power | investment | 834.6 | $/kW | 25 | Power Equipment | p.101 (p.123) | 1000 | 24 | 2021
LowT-Molten-Salt-Energy | investment | 17.67 | $/kWh | 25 | EPC fee | p.101 (p.123) | 1000 | 24 | 2021
LowT-Molten-Salt-Energy | FOM | 0.25327 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
LowT-Molten-Salt-Power | FOM | 3.5888 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
LowT-Molten-Salt-Power | efficiency | 0.514 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2021
LowT-Molten-Salt-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
LowT-Molten-Salt-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
Concrete-Energy | investment | 20.74 | $/kWh | 25 | SB and BOS, 0.85 of 2021 value | p.98 (p.120) | 1000 | 24 | 2030
Concrete-Power | investment | 808.45 | $/kW | 25 | Power Equipment, 0.95 of 2021 value | p.98 (p.120) | 1000 | 24 | 2030
Concrete-Energy | investment | 6.222 | $/kWh | 25 | EPC fee, Project Development, Grid integration | p.98 (p.120) | 1000 | 24 | 2030
Concrete-Energy | FOM | 0.089182 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
Concrete-Power | FOM | 3.4763 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2030
Concrete-Power | efficiency | 0.43 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2030
Concrete-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
Concrete-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2030
Concrete-Energy | investment | 24.4 | $/kWh | 25 | Molten Salt SB and BOS | p.101 (p.123) | 1000 | 24 | 2021
Concrete-Power | investment | 1029.6 | $/kW | 25 | Power Equipment | p.101 (p.123) | 1000 | 24 | 2021
Concrete-Energy | investment | 8 | $/kWh | 25 | EPC fee | p.101 (p.123) | 1000 | 24 | 2021
Concrete-Energy | FOM | 0.10492 | $/kWh-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
Concrete-Power | FOM | 4.4273 | $/kW-year | 25 | not provided, calculated as for hydrogen | p 104 (p.126) | 1000 | 24 | 2021
Concrete-Power | efficiency | 0.41 |  | 25 | RTE, assume 99% for charge, and other for discharge | p.107 (p.129) | 1000 | 24 | 2021
Concrete-Power | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021
Concrete-Energy | lifetime | 35 | years | 25 |  | p.107 (p.129) | 1000 | 24 | 2021